# From PID to Predictive: A Layered How‑To for PLC + MPC + ML (v2)

Whiskey House — Controls & Data Team · August 14, 2025

From PID to Predictive: A Layered How‑To for PLC + MPC + ML (v2)

Author: Whiskey House — Controls & Data Team

Date: August 14, 2025

# 1. Executive Summary & Goals

This guide shows how to evolve a PLC loop from classical PID/PIDE to a three‑layer architecture:

Layer 1: PLC PIDE (cascade + feed‑forward)

Layer 2: MPC overlay for complex/interactive loops

Layer 3: ML supervisory layer for prediction, soft sensing, and adaptive policies

Outcomes: tighter control (reduced IAE), less saturation, better quality stability, and auditable guardrails.

# 2. Layered Architecture (Overview)

Control flow:

• Operators set business targets (quality, throughput, energy).

• ML predicts disturbances / quality and recommends weights or SPs to MPC.

• MPC computes optimal setpoints for Layer 1 within constraints.

• Layer 1 actuates valves/drives (PIDE) with anti‑windup and cascade tracking.

Data flow:

• PLC → Historian/Message bus (PV, CV, SP, DV, states) → ML/MPC runtime

• Runtime → PLC (SPs, bias, mode requests) via OPC UA/MQTT/EIP under allow‑lists.

Safety:

• Hard PLC interlocks remain authoritative.

• MPC/ML only supervise; clean fallback to Layer 1 is always available.

# 3. Layer 1 — PIDE (Rockwell FBD preferred)

3.1 Wiring Essentials

• Primary (outer) PIDE PV = Vent temperature; CV = inner SP (engineering units of °F).

• Secondary (inner) PIDE PV = Product condenser temp; CV = cooling water valve %.

• Enable Cascade/Ratio (AllowCasRat=TRUE). Wire outer.CV → inner.SPCascade.

• Use BKCAL/External Reset between loops to prevent primary outrunning secondary.

• Use CVInitReq/CVInitValue to ensure bumpless transfers when modes change.

• Apply feed‑forward bias at the inner PIDE Bias input; clamp and low‑pass noisy DVs.

3.2 Tasking & Timing

• Inner task: 300–500 ms (start at 400 ms), priority 5–7; RPI of PVs < task period.

• Outer task: 1.5–2.0 s (start at 1.8 s), priority 8–10; executes after inner within scan.

3.3 Feed‑Forward Bias (example scales; tune from field data)

• DV1 PIT‑4012 (vapor pressure, psi): bias_p = 0.075 × (psi)

• DV2 TIT‑52001 (cooling temp, °F):   bias_t = 0.0086 × (T − 67.5)

• DV3 PIT‑52006 (cooling pressure):   bias_c = 0.25 − ((P − 25)/70)

• Total_Bias = clamp(bias_p + bias_t + bias_c, −0.30, +0.30)

• Apply first‑order filter to each DV: y[k] = y[k−1] + α (x[k] − y[k−1]), α≈0.1–0.2

3.4 IMC / Lambda Tuning (PI form; first‑order‑plus‑dead‑time model Gp(s)=Kp * exp(-theta*s)/(tau*s+1))

• Choose lambda ≈ 2*theta … 3*theta for thermal loops.

• IMC PI:  Kc = tau / (Kp * (lambda + theta));  Ti = tau

• Workflow: step tests (manual CO steps) → fit Kp, tau, theta → compute Kc, Ti → implement → refine.

# 4. Layer 2 — MPC Overlay

4.1 Scope & Role

• Supervisory SP generator that respects constraints and anticipates disturbances.

• Keeps SPs feasible; penalizes valve movement; can optimize energy/quality tradeoff.

4.2 Modeling Choices

• Linear state‑space (N4SID/MOESP) or ARX/ARMAX for fast identification.

• Include measured DVs (vapor pressure, cooling supply T/P, beer feed/steam swings).

4.3 MPC Spec (template)

• MV: Inner loop SP (°F) or direct valve % (if bypassing cascade during tests).

• CVs: Vent temp (target band 151–155°F), optionally product temp.

• DVs: PIT‑4012, TIT‑52001, PIT‑52006, beer feed, steam flow, column pressure.

• Constraints:  valve 0–100%; rate limits; SP bounds; CV high/low alarms.

• Horizons:  prediction Np=30–60, control Nc=5–10 (tune vs task period).

• Objective:  w1·|CV−SP_ref| + w2·ΔMV + w3·energy; hard constraint handling.

4.4 Handoff & Fallback

• MPC writes inner.SPCascade (or outer.SP) within clamps; PLC validates.

• If infeasible/no data/latency breach → hold last good SP or drop to operator SP.

• Record every SP update with provenance (model version, constraints active).

# 5. Layer 3 — ML Supervisory

5.1 Use Cases

• Soft sensors: proof, composition proxies, condenser load.

• Disturbance prediction: short‑term forecasts of vapor load & cooling capacity.

• Adaptive policies: suggest lambda, Kc, Ti trims or MPC weight tweaks under guardrails.

5.2 Data & MLOps

• Schema: timestamped PV/CV/SP/DV/states; synchronized and validated.

• Latency budget: inference < 100 ms at edge; fall back when exceeded.

• Drift: monitor error & feature shift; retrain monthly/seasonally or when KPIs slip.

• Guardrails: ML never commands AO; only recommends SP/weights within PLC clamps.

# 6. Still01 Worked Example (LWC/LWVC)

6.1 Layer 1 (Cascade + FF PIDE)

• Outer PV: TIT‑4031 (vent temp), SP=153°F; Outer CV→ Inner SP (°F range ~85–165°F).

• Inner PV: TIT‑4033; Inner CV: FCV‑4032 %; Bias from PIT‑4012/TIT‑52001/PIT‑52006.

• Commissioning: tune inner (manual steps), then cascade, then enable bias.

6.2 Layer 2 (MPC)

• MV: Inner SP; CV: vent temp; DVs as above; constraints: valve %, SP bounds, ROC.

• Start with ARX model; validate on step‑test data; then move to N4SID if MIMO.

6.3 Layer 3 (ML)

• Train LSTM/NARX on historian to predict +2–5 min vapor pressure and proof proxy.

• Feed prediction to MPC as preview DV or adjust objective weights.

6.4 KPIs & Checks

• KPI: vent temp in band (>98% of time), IAE↓, CV saturation↓, settling time↓.

• Alarms: use ALMA with HH/H/L/LL; shelve & unshelve logic per SOP.

# 7. Commissioning Checklists (condensed)

7.1 Layer 1

☐ AI scaling & calibration; PVFault handling

☐ Inner tuning complete; ROC limits; saturation flags visible

☐ Outer cascade wiring; BKCAL/External reset verified

☐ Bias scaling & clamps; DV filters tuned; season offsets noted

7.2 Layer 2

☐ Step tests captured; model fit validated; horizons set

☐ Constraint set verified; infeasibility handling tested

☐ Fallback to Layer 1 clean; provenance logging active

7.3 Layer 3

☐ Dataset schema & validation; training split; latency budget

☐ Drift monitors; retrain cadence; human-in-the-loop signoff

☐ Guardrails enforced (no direct AO); audit logs

# 8. Troubleshooting (quick cues)

• Oscillation after cascade enable → check BKCAL/exec order/ROCs.

• Bias “fights” PID → clamp lower, filter DVs, confirm units.

• MPC chattering → increase w(ΔMV), tighten rate limits, lengthen Nc.

• ML suggestions off → stale model; retrain or roll back to last green version.

## Appendix A — Formulas & Tables

• IMC PI: Kc = tau / (Kp * (lambda + theta)); Ti = tau;  lambda ≈ 2*theta…3*theta (thermal)

• FF filter: y[k] = y[k−1] + alpha * (x[k] − y[k−1])

• Sample inner PI starting point: Kc≈1.0; Ti≈60–120 s; outer Kc≈0.5×inner; Ti≈300 s (retune via IMC).

## Appendix B — Tag & Pin Map (abbrev)

• Outer PIDE: PV=TIT_4031; CV→Inner.SPCascade; SP=operator (153°F)

• Inner PIDE: PV=TIT_4033; CV=FCV_4032 %; Bias=FF_total; BKCAL linked

• DVs: PIT_4012, TIT_52001, PIT_52006 (+ beer feed, steam, column pressure as needed)