Model-Based Tuning: IMC and Lambda Methods

1.      Why Choose IMC or Lambda Tuning Instead of Trial-and-Error?

1.1.     Trial-and-error tuning often results in:

    - Excessively aggressive or overly conservative control.

    - Poor disturbance rejection.

    - Integral windup issues.

  - Unstable performance if process conditions change.

- IMC (Internal Model Control) and Lambda tuning - are structured, model-based approaches that clearly relate controller settings (Kc, Ti, Td) to measurable process dynamics: dead time (θ), time constant (τ), and process gain (Kp).

  - These methods deliver controllers that:

    - Robustly handle disturbances.

    - Gracefully manage systems with dead time.

    - Provide predictable, stable, closed-loop control.

  - When to use IMC:

    - Process dead time (θ) and time constant (τ) are clearly know or measurable.

    - Process stability and Robustness matter more than extreme responsiveness.

    - Reliable disturbance rejection and minimal overshoot are desired.

3. Process Model (FOPDT): IMC and Lambda tuning typically utilize a First Order Plus Dead Time (FOPDT) model to approximate the process: Gp​(s) = Kp​ e^-θs​ / τs+1

3.1. Where:

    - Gp​(s) = Process transfer f(x). It describes how input signals are converted to output signals in the Laplace domain.

    - s = time in seconds.

    - Kp = Process gain (ΔPV / ΔCO).

    - τ (Tau) = Process time constant (speed of PV response).

    - θ (Theta) = Dead time (delay between action and process response).

  - Key Process Parameters:

    - Process Gain (Kp): Defined as the change in the process variable (PV) divided by the change in controller output (CO): Kp​= ΔPV / ΔCO.

    - Time Constant (τ): Represents how quickly the PV responds to a change.

      - A smaller τ indicates a faster response, while a larger τ means slower response.

    - Dead Time (θ): The delay before any noticeable change in PV after a change in CO is introduced. Also referred to as "transport delay" or "process lag."

    - Desired Closed-Loop Time Constant (λ): A chosen parameter that dictates the desired response speed and stability of the closed-loop system:

      - Smaller λ: Faster, more aggressive control.

      - Larger λ: Slower, more stable and robust control.

3.3. Rule of Thumb for Thermal Processes: Set λ between two to three times the dead time: λ = 2θ to 3θ.

4. IMC Tuning Formulas for PI Controllers: IMC tuning aims to counteract process dynamics by using a simplified internal model plus a low-pass filter for enhanced stability.

4.1. Proportional Gain (Kc): Kc​= τ  / (Kp​×(λ+θ)) ​

4.2. Integral Time (τi): set to the process time constant – τi = τ

5. Practical Steps for Controller Tuning:

5.1. Conduct a Step Test

5.1.1. Set controller to manual mode.

5.1.2. Apply a small, known step change in controller output (CO).

    - Record how the process variable (PV) responds over time.

  - Determine Process Parameters from Step Test

    - Kp: Change in PV divided by change in CO.

    - τ: Time for PV to reach ~63% of its total response.

    - θ: Delay before PV begins responding.

  - Select Desired Closed-Loop Time Constant (λ)

    - Choose λ based on desired balance of response speed and stability.

    - For thermal processes, a common starting point is λ = 2θ to 3θ.

  - Compute Controller Settings

    - Input Kp, τ, θ, and λ into the IMC tuning formulas to calculate Kc and τi.

  - Implement and Test Controller Settings

    - Enter computed Kc and τi values into the PI controller.

    - Monitor system performance.

    - Adjust λ if necessary for desired performance.

6. Additional Resources

For further reading and deeper understanding:

- Tuning Control Loops with the IMC Tuning Method

- Fundamentals of Lambda Tuning

- PID Control Fundamentals