Quick Start Guide – cascaded ff control loop instantiation.

The detailed guide for this process can be found in Supporting Documents in Section 10, below.

Definitions and Key Acronyms:

- PV: Process Variable(s)

  - PPV: Primary Process Variable

  - SPV: Secondary Process Variable

- DV: Disruptive Variable(s)

- SP: Setpoint

- CV: Control Variable

- PIDE: Proportional-Integral-Derivative Enhanced controller

- FBD: Function Block Diagram

- Bias: Preemptive adjustment to controller output based on anticipated process disturbances

- Objective: Work thru a specific example – Still01 LWC / LWVC Control Loop

  - Maintain vent condenser temp (TIT-4031) at 151–155 °F.

  - Condense ethanol while venting methanol via automated cooling control.

- Key Components

  - Primary PIDE (Outer Loop I Secondary PV (SPV)): Monitors TIT-4031; sets SP for inner loop.

    - SPV: TIT-4031

    - SP: 153°F (target midpoint)

    - CV: Sets SP for Inner Loop

  - Secondary PIDE (Inner Loop): Controls TIT-4033 by adjusting FCV-4032.

    - PPV: TIT-4033

    - SP: Provided by Outer Loop

    - CV: Cooling valve command (FCV-4032)

  - Feedforward Input: Adjusts valve CV based on PIT-4012 (vapor pressure), TIT-52001 (cooling temp), PIT-52006 (cooling pressure).

    - DV: PIT4012 (Vapor Pressure): Bias = 0.075 × Pressure (psi)

    - DV: TIT52001 (Cooling Temp.): Bias = 0.0086 × (Temp – 67.5°F)

    - DV: PIT52006 (Cooling Pressure): Bias = 0.25 – ((Pressure – 25)/70)

    - Total_Bias = Total Bias = 1 + PIT4012.bias + TIT52001.bias + PIT52006.bias

    - Note: Bias constants are historical starting points requiring regular validation and adjustment.

    - Important: Utilize Studio 5000 PIDE block built-in anti-windup features to prevent CV saturation. More on this topic here.

Architecture Diagram: simplified block diagram:

- Implementation in Studio 5000: PIDE Configuration (Function Block preferred)

  - Inner Loop: Periodic task @ 400ms, Priority: 5–7

    - SP Source = SPCascade input

    - Mode = CASCADE

    - Bias input wired to feedforward total

    - **Ensure: PV Input RPI < Task time (recommend 100ms)

  - Outer Loop: Periodic task @ 1.8s, Priority: 8–10

    - CV = Inner Loop SP

    - Mode = CASCADE

    - CVInitReq logic for manual transitions

    - Feedforward Wiring:

      - Use SCL blocks to scale PIT-4012, TIT-52001, and PIT-52006

      - Combine into a single Bias signal and clamp it if needed

  - NOTE: Task Scheduling & Timing: Place each PIDE instruction in separate periodic tasks to allow independent adjustments. Collect and use baseline response data (worksheet provided) to refine these intervals.

  - Scheduling best practices:

    - Outer loop must update after inner loop in same scan.

    - In FBD, execution order is preserved left to right.

- Tuning Methodology

  - Data Collection: **Baseline data MUST be collected before moving to the Advanced Control Loop.  Using existing PID populate the necessary data points (outlined in: Supporting Documents in Section 10).

  - New Control Loop Initialization & Tuning:  Using the data obtained from baseline data collection workbook, we can instantiate the new control mechanisms and set them up for testing.

    - Inner Loop: Manual valve step → record TIT-4033 response.

    - Outer Loop: Manual inner SP step → record TIT-4031 response.

    - Feedforward: Increase vapor pressure → log temperature response.

  - Tuning Recommendations:

    - Inner Loop: Kc ≈ 1.0; Ti ≈ 60–120s

    - Outer Loop: Kc ≈ 0.5 of Inner; Ti ≈ 300s

- Structured Model-Based Tuning (IMC & Lambda Methods):

  - Initial tuning parameters are preliminary:

    - Inner Loop: Kc ≈ 1.0; Ti ≈ 60–120s

    - Outer Loop: Kc ≈ 0.5 (of Inner loop); Ti ≈ 300s

  - Refine these values using IMC or Lambda tuning methods as detailed in the "Model-Based Tuning" supporting document.

    - IMC/Lambda methods ensure stable, robust, predictable disturbance handling.

- Commissioning & Monitoring - Deployment Steps:

  - Set loops in manual; stabilize process.

  - Enable inner PIDE (CAS → Auto); confirm stable product temp.

  - Enable outer PIDE (CAS); verify bumpless transfer.

  - Confirm bias logic correct via disturbance injection tests.

- Validation - Watch for:

  - Valve saturation: CV @ 0 or 100% while in Auto.

  - TIT-4031 drifting outside 151–155 °F, for longer than 10s

  - Feedforward not reacting effectively.

- Long-Term Monitoring:

  - Seasonally adjusts to feedforward constants (TIT-52001, PIT-52006).

  - Regularly update bias formula with field data.

  - Use loop performance indicators: IAE, settling time, valve activity.

- Supporting Documents:

  - Cascaded Feedforward PIDE Control for Still01 Low Wine Condensers.docx

  - Model Based Tuning.docx

  - Loop data collection table (1).xlsx